## Slide 1
POWER TRANSFORMER HEALTH
Condition-Monitoring Dataset — Statistical Analysis
500 records · 15 fields · 11 kV fleet · Ages 2–30 years
Charts | Distributions | Correlations | Model Metrics

## Slide 2
Transformer Health Analytics | Statistical Review
2 / 11
CONTEXT
5W + 1H at a glance
WHAT
500 transformer sensor readings + Health label (Healthy / Warning / Critical)
WHO
Utilities, industry, renewables, rail traction — reliability teams
WHERE
Distribution substations & industrial step-down transformers
WHEN
Single snapshot · units aged 2–30 years · mixed fleet condition
WHY
Predictive maintenance before failure · condition-based overhaul planning
HOW
RTD · DGA · vibration · PD sensors → Random Forest (96.8% accuracy)

## Slide 3
Transformer Health Analytics | Statistical Review
3 / 11
FLEET DISTRIBUTION
Health status split — 500 transformers
Chart: 
| Healthy | Warning | Critical
Health | 155 | 223 | 122
Healthy
155
31% of fleet · Avg age 8.3 yrs
Warning
223
44.6% of fleet · Avg age 14.0 yrs
Critical
122
24.4% of fleet · Avg age 25.4 yrs

## Slide 4
Transformer Health Analytics | Statistical Review
4 / 11
PARAMETER COMPARISON
Average values by health status — clear separation
Chart: 
| Age | Oil °C | Wind °C | Load % | Moist | Gas | Vib | PD
Healthy | 8.3 | 68.1 | 77.8 | 51.6 | 15.4 | 22.3 | 2.39 | 33.5
Warning | 14 | 79.3 | 89.4 | 73.4 | 20.5 | 32.5 | 3.19 | 51.8
Critical | 25.4 | 84.1 | 93.6 | 75.7 | 29.6 | 44.6 | 4.2 | 75.7

## Slide 5
Transformer Health Analytics | Statistical Review
5 / 11
STRESS INDICATORS
Thermal · Dielectric · Mechanical — group averages
Thermal (°C)
Chart: 
| Oil | Winding
Healthy | 68.1 | 77.8
Warning | 79.3 | 89.4
Critical | 84.1 | 93.6
Dielectric
Chart: 
| Moisture | Gas/10 | PD
Healthy | 15.4 | 22.3 | 33.5
Warning | 20.5 | 32.5 | 51.8
Critical | 29.6 | 44.6 | 75.7
Mechanical & Load
Chart: 
| Vib | Load% | OilLvl
Healthy | 2.39 | 51.6 | 96.1
Warning | 3.19 | 73.4 | 93.8
Critical | 4.2 | 75.7 | 89.4

## Slide 6
Transformer Health Analytics | Statistical Review
6 / 11
CORRELATION WITH HEALTH DECLINE
Ranked by absolute correlation coefficient
Chart: 
| Dissolved Gas | Vibration | Partial Disc. | Oil Temp | Winding Temp | Age | Moisture | Load/Current | Oil Level* | Ambient
Correlation | 0.83 | 0.82 | 0.82 | 0.75 | 0.73 | 0.7 | 0.7 | 0.48 | 0.65 | 0.08

## Slide 7
Transformer Health Analytics | Statistical Review
7 / 11
RANDOM FOREST PERFORMANCE
96.8% accuracy · 125-unit held-out test set
96.8%
Overall Accuracy
Chart: 
| Critical | Healthy | Warning
Precision | 0.97 | 1 | 0.95
Recall | 0.93 | 0.97 | 0.98
F1-Score | 0.95 | 0.99 | 0.96
Top Feature Importance (model weight)
Vibration
22%
Oil / Winding Temp
21%
Dissolved Gas
20%
Partial Discharge
14%
Moisture + Age
13%
Load / Other
10%

## Slide 8
Transformer Health Analytics | Statistical Review
8 / 11
ASSET EXAMPLES
Transformer IDs by health status
CRITICAL · 122
T0006
T0007
T0011
T0015
T0016
T0017
T0021
T0023
T0027
T0028
T0042
T0085
T0113
T0213
T0287
WARNING · 223
T0001
T0002
T0005
T0008
T0009
T0010
T0012
T0018
T0019
T0020
T0024
T0036
T0044
T0052
T0066
HEALTHY · 155
T0003
T0004
T0013
T0014
T0022
T0025
T0030
T0032
T0033
T0034
T0035
T0043
T0051
T0056
T0068

## Slide 9
Transformer Health Analytics | Statistical Review
9 / 11
FLEET SUMMARY STATISTICS
Mean · Std Dev · Range across 500 units
Parameter | Mean | Std | Min | Max
Age (Years) | 15.0 | 8.8 | 2 | 30
Oil Temp (°C) | 77.0 | 8.0 | — | 96.4
Winding Temp (°C) | 86.8 | 8.3 | — | 105.8
Current (A) | 302 | 87 | — | 457
Load (%) | 67.2 | 19.3 | — | 100
Oil Level (%) | 93.5 | 3.8 | — | 100
Moisture (ppm) | 21.1 | 7.4 | — | 36
Dissolved Gas (ppm) | 323 | 99 | — | 557
Vibration (mm/s) | 3.19 | 0.81 | — | 5.04
Partial Discharge (pC) | 51.9 | 19.0 | — | 94.4

## Slide 10
Transformer Health Analytics | Statistical Review
10 / 11
KEY NUMBERS & ACTIONS
What the data says to do next
0.83
Top correlation
(Dissolved Gas)
96.8%
Model accuracy
(held-out test)
24%
Fleet already
in Critical
3
Dominant drivers
Gas · Vib · PD
Immediate actions
1. Prioritise units with rising Dissolved Gas or Partial Discharge → e.g. T0023, T0085, T0213, T0287
2. Investigate high vibration promptly — strongest single predictor of mechanical issues
3. Cross-check falling oil level + rising moisture for possible seal leaks
4. Deploy model as triage layer; add gas-by-gas DGA and trend rates for production use

## Slide 11
SUMMARY
Sensor data cleanly separates health tiers.
Model automates classification at 96.8% accuracy.
Focus maintenance on gas, vibration and PD trends.
Questions?