## Slide 1
POWER TRANSFORMER HEALTH
Condition-Monitoring Dataset — Statistical Analysis Report
500 records · 15 fields · 11 kV distribution-class fleet
Senior Electrical Design Engineering Review
Predictive Maintenance | Asset Health Scoring | DGA · Thermal · Mechanical Indicators

## Slide 2
Transformer Health Analytics | Engineering Review
2 / 12
CONTEXT FRAMEWORK
5W + 1H — Framing the Transformer Health Analysis
WHAT
500-record condition-monitoring telemetry for 11 kV distribution transformers: electrical, thermal, mechanical & dielectric sensors + Health_Status label (Healthy / Warning / Critical).
WHO
Electric utilities, industrial plants (steel, cement, data centers), renewable energy sites, railway traction substations — asset managers & reliability engineers.
WHERE
Distribution & sub-transmission substations; dedicated step-down transformers in industrial facilities; wind/solar step-up transformers.
WHEN
Snapshot dataset (one reading per unit). Ages 2–30 years. Reflects an aging, mixed-condition fleet suitable for model training & triage prioritization.
WHY
Enable predictive maintenance: detect insulation degradation, thermal stress & mechanical issues before catastrophic failure; shift from time-based to condition-based maintenance.
HOW
Online sensors (RTDs, DGA, vibration, PD) feed a health-scoring platform. Random Forest (96.8% accuracy) reproduces labels from 11 numeric sensors + cooling status.

## Slide 3
Source: transformer_health_dataset_500_records.csv
3 / 12
DATASET STRUCTURE
15 fields · 500 transformers (T0001–T0500) · mixed ages 2–30 years
Identifier
Transformer_ID
Thermal
Oil Temp · Winding Temp · Ambient Temp
Electrical / Load
Voltage (11 kV) · Current · Load %
Insulation / Dielectric
Moisture ppm · Dissolved Gas ppm · PD pC
Mechanical / Integrity
Vibration mm/s · Oil Level %
Operational / Target
Cooling Status · Health_Status
500
Records
15
Fields
11 kV
Voltage Class
2–30
Age Range (yrs)

## Slide 4
Transformer Health Analytics | Engineering Review
4 / 12
FLEET HEALTH DISTRIBUTION
Nearly 1 in 4 units Critical; almost half in Warning — aging fleet profile
Chart: 
| Healthy (31%) | Warning (44.6%) | Critical (24.4%)
Health | 155 | 223 | 122
Healthy
155
31.0% of fleet
Avg age 8.3 yrs
Warning
223
44.6% of fleet
Avg age 14.0 yrs
Critical
122
24.4% of fleet
Avg age 25.4 yrs

## Slide 5
Transformer Health Analytics | Engineering Review
5 / 12
DESCRIPTIVE STATISTICS
Fleet-wide summary — values consistent with 11 kV distribution transformers
Parameter | Mean | Std Dev | Min | Max
Age (Years) | 15.0 | 8.83 | 2 | 30
Oil Temperature (°C) | 77.0 | 8.04 | — | 96.4
Winding Temperature (°C) | 86.8 | 8.28 | — | 105.8
Ambient Temperature (°C) | 30.2 | 6.91 | — | 42
Current (A) | 302.2 | 86.8 | — | 457.3
Load (%) | 67.2 | 19.3 | — | 100
Oil Level (%) | 93.5 | 3.77 | — | 100
Moisture (ppm) | 21.1 | 7.40 | — | 36
Dissolved Gas (ppm) | 323.0 | 98.7 | — | 557
Vibration (mm/s) | 3.19 | 0.81 | — | 5.04
Partial Discharge (pC) | 51.9 | 19.0 | — | 94.4

## Slide 6
Transformer Health Analytics | Engineering Review
6 / 12
PARAMETER BEHAVIOR BY HEALTH STATUS
Every key stress indicator rises monotonically: Healthy → Warning → Critical
Parameter | Healthy | Warning | Critical | Trend
Age (yrs) | 8.3 | 14.0 | 25.4 | Strong ↑
Oil Temp (°C) | 68.1 | 79.3 | 84.1 | Strong ↑
Winding Temp (°C) | 77.8 | 89.4 | 93.6 | Strong ↑
Current (A) | 232.2 | 330.2 | 340.0 | Strong ↑
Load (%) | 51.6 | 73.4 | 75.7 | Strong ↑
Oil Level (%) | 96.1 | 93.8 | 89.4 | Falls ↓
Moisture (ppm) | 15.4 | 20.5 | 29.6 | Strong ↑
Dissolved Gas (ppm) | 223.4 | 325.1 | 445.5 | Strong ↑
Vibration (mm/s) | 2.39 | 3.19 | 4.20 | Strong ↑
Partial Discharge (pC) | 33.5 | 51.8 | 75.7 | Strong ↑

## Slide 7
Transformer Health Analytics | Engineering Review
7 / 12
CORRELATION WITH HEALTH DECLINE
Dissolved gas, vibration & partial discharge dominate (r ≥ 0.82)
Dissolved Gas (ppm)
Very Strong
+0.83
Vibration (mm/s)
Very Strong
+0.82
Partial Discharge (pC)
Very Strong
+0.82
Oil Temperature (°C)
Strong
+0.75
Winding Temperature (°C)
Strong
+0.73
Age (Years)
Strong
+0.70
Moisture (ppm)
Strong
+0.70
Load % / Current (A)
Moderate
+0.48
Oil Level (%)
Strong (inverse)
−0.65
Ambient Temperature (°C)
Negligible
+0.08

## Slide 8
Transformer Health Analytics | Engineering Review
8 / 12
PREDICTIVE MODEL — RANDOM FOREST
96.8% accuracy on held-out test set (125 transformers) — only adjacent-tier errors
Critical
Support: 30
Precision
0.97
Recall
0.93
F1-Score
0.95
Healthy
Support: 39
Precision
1.00
Recall
0.97
F1-Score
0.99
Warning
Support: 56
Precision
0.95
Recall
0.98
F1-Score
0.96
Model Configuration & Key Observations
• Random Forest: 300 trees, max depth 8 · 75/25 stratified train/test split · 11 numeric sensors + encoded Cooling_Status
• Overall accuracy 96.8% — only 4 of 125 misclassified; all errors were to adjacent severity tier (no Healthy↔Critical swaps)
• Dominant features: Vibration, Oil/Winding Temperature, Dissolved Gas (~2/3 of decision weight) — aligns with known fault mechanisms

## Slide 9
Transformer Health Analytics | Engineering Review
9 / 12
ASSET IDENTIFIERS BY HEALTH STATUS
Representative Transformer IDs — triage examples from the 500-unit fleet
CRITICAL (122)
Immediate attention required
T0006 T0007 T0011 T0015 T0016 T0017 T0021 T0023 T0027 T0028 T0042 T0085 T0113 T0213 T0287
WARNING (223)
Elevated risk — schedule inspection
T0001 T0002 T0005 T0008 T0009 T0010 T0012 T0018 T0019 T0020 T0024 T0036 T0044 T0052 T0066
HEALTHY (155)
Within normal operating envelope
T0003 T0004 T0013 T0014 T0022 T0025 T0030 T0032 T0033 T0034 T0035 T0043 T0051 T0056 T0068

## Slide 10
Transformer Health Analytics | Engineering Review
10 / 12
KEY FINDINGS
Statistical signals map cleanly onto established transformer failure mechanisms
01
Composite Health Score
Health_Status is driven primarily by dissolved gas, vibration, and partial discharge — the three classic incipient-fault indicators in transformer diagnostics.
02
Age is Strong but Not Dominant
Critical units average 25.4 yrs vs 8.3 yrs for Healthy, yet some older units remain Healthy — maintenance history and loading matter more than age alone.
03
Load Has Diminishing Marginal Signal
Warning and Critical units carry nearly identical average load (73–76%). Thermal and dielectric indicators separate the two worst tiers, not load alone.
04
Oil Level is the Inverse Indicator
Only parameter that falls with worsening health (96% → 89%), consistent with gasket/seal degradation on older, more stressed units.
05
Cooling Status is Reactive
Fan/pump running vs Normal has only 0.4% feature importance — active cooling engages with load, not as a leading health indicator.
06
High Model Separability
Random Forest reaches 96.8% accuracy; sensor set is sufficient for automated real-time health-scoring dashboards and alarm systems.

## Slide 11
Transformer Health Analytics | Engineering Review
11 / 12
RECOMMENDATIONS
Maintenance prioritization and production-deployment guidance
MAINTENANCE PRIORITIZATION
Prioritize rising Dissolved Gas or PD trends over pure load or ambient flags.
Investigate vibration anomalies promptly — strongest single predictor; often signals core/winding looseness.
Cross-check moisture-in-oil with oil level: falling oil + rising moisture may indicate seal leak and moisture ingress.
Treat Critical-tier units (e.g. T0023, T0085, T0213, T0287) as highest priority for outage planning.
PRODUCTION DEPLOYMENT
Validate against laboratory DGA results before automated alarms — online sensors are typically less precise than lab DGA.
Add gas-by-gas breakdown (H₂, CH₄, C₂H₂, C₂H₄, C₂H₆, CO, CO₂) to distinguish thermal vs electrical vs arcing faults.
Track rate-of-change (ppm/month) — stronger early-warning signal than absolute snapshot levels.
Use model as triage layer; retain engineering judgment for final maintenance decisions.

## Slide 12
Transformer Health Analytics | Engineering Review
12 / 12
CONCLUSION
Sensor suite is sufficient for automated health scoring; trend data remains the key gap
96.8%
Model Accuracy
0.83
Top Correlation
(Dissolved Gas)
24.4%
Fleet in
Critical State
This dataset is well-structured for predictive-maintenance analytics on a distribution transformer fleet. The health label is statistically well explained by thermal, dielectric, and mechanical sensor readings — consistent with established transformer failure mechanisms. A Random Forest classifier reproduces labeling at 96.8% accuracy, confirming the sensor set supports automated health-scoring. The principal limitation for real-world deployment is the absence of time-series trend data and validated laboratory DGA cross-checks. On a single-snapshot basis, the data supports strong triage-level decision-making for maintenance prioritization.